## Example 15-30
Example 15-30. Line Sizes for Flashing Steam Condensate by A.K. Coker
The spreadsheet calculates the following:
1. The amount of condensate flashed for any given condensate header pressure from 15 to 140 psia
and initial steam pressures may vary between 40 and 165 psia.
2. The return condensate header temperature.
3. The pressure drop (psi/100 ft) of the steam condensate mixturea in the return header.
4. The velocity of the steam condensate mixture
5. Indicates a warning message if velocity is equal to or greater than 5000 ft/min.
Nomenclature
D= | Pipe internal diameter, inch.
DELTP= | Pressure drop of flashed condensate mixture, psi/100 ft
DENG= | Flashed steam density, lb/ft3
DENL= | Flashed condensate liquid density, lb/ft3
DENMIX= | Density of mixture (Flashed condensate/steam, lb/ft3 )
FF= | Friction factor
PC= | Steam condensate pressure before flashing, psia
PH= | Flashed condensate header pressure, psia
TFL= | Temperatur of flashed condensate mixture, oF
VEL= | Velocity of flashed condensate mixture, ft/min.
W= | Total flow of mixture in condensate header, lb/h
WFRFL= | Weight fraction of condensate flashed to vapor
WG= | Flashed steam flow rate, lb/h
WL= | Flashed condensate liquid flow rate, lb/h
Solution:
W= | 10000 | lb/h
PC= | 114.7 | psia
PH= | 14.7 | psia
G= | 32.2 | ft/sec2
Calculate the weight fraction of condensate flashed to vapor
X= | -0.17263
A= | 0.06331
B= | 0.0088841
WFRFL= | 0.13649
WG= | 1364.9105 | lb/h
WL= | 8635.0895 | lb/h
Calculate the temperature of flashed condensate.
TFL= | 212.3596 | Of
Calculate the Flashed Steam density, flashed condensate liquid, and density of mixture
DENG= | 0.036086 | lb/ft3
DENL= | 59.78 | lb/ft3
DENMIX= | 0.26338 | lb/ft3
| PIPE SIZE |  |  | 4 inch | 6inch | 8 inch
|  |  | I.D, in.= | 4.026 | 6.065 | 7.981
|  |  | I.D, ft= | 0.3355 | 0.50542 | 0.66508
|  |  | Area, ft2= | 0.088405 | 0.20063 | 0.34741
| Friction factor, f= |  |  | 0.016284 | 0.0149 | 0.014069
| Pressure drop, DELPT= |  |  | 1.964 | 0.23162 | 0.21871 | psi/100 ft
| Velocity of flashed |  |  | 7153.8432 | 3152.2841 | 1820.4231 | ft/min
condensate mixture:
| Warning: If V ≥ 5000 ft/min |  |  | Pipe deterioration is possible
| condensate may cause |  |  |  | no pipe deterioration
| deterioration of the process |  |  |  |  | no pipe deterioration
pipeline