## Example 16-25
Example 16-25. Revised Performance Calculations of Centrifugal Pump for Handling Oil by A.K. Coker
Figure 16-62 shows the performance curve of a centrifugal pump operated on water. If the same
pump is used for handling oil with a specific gravity of 0.9 and a viscosity of 1000SSU (220cSt)
at the pumping temperature, develop the performance curve of the same pump for oil.
Solution
Figure 16-62 shows the performance curve of a centrifugal pump operated on water. If the same
pump is used for handling oil with a specific gravity of 0.9 and a viscosity of 1000SSU (220cSt)
at the pumping temperature, develop the performance curve of the same pump for oil.
Using Figure 16-62 for water, locate the best efficiency point (BEP), it is 170 m3/h. For water
with 170m3/h capacity, the pump efficiency is a maximum at 86%. Tabulate capacity, head and
efficiency for 0.6 x 170, 0.8 x 170, and 1.2 x 170 m3/h. From Figure 16-62, at 170 m3/h, the
head developed by the pump is 31m. Using Figure 16-59c, the viscosity correction factor at 170
m3/h capacity is obtained as follows:
Draw a vertical line until it intercepts 31 m head
Then a horizontal line along the capacity axis until it intercepts 1000 SSU (220cSt) viscosity parallel lines.
Then draw a vertical line to the correction factors scale on Figure 16-59c, and read the correction
factors at CE, CQ and CH (0.6 x QN, 0.8 x QN, 1.0 x QN and 1.2 x QN) respectively.
CE | 0.645
CQ | 0.95
CH | = 0.96 (for 0.6 x QN)
CH | = 0.94 (for 0.8 x QN)
CH | = 0.92 (for 1 x QN)
CH | = 0.895 (for 1.2 x QN)
For 0.6 x QNW calculations
QNW = 170 m3/h
0.6 x QNW = 0.6 x 170 = 102 m3/h
Using 102 m3/h from Figure 16 – 62,
The head Hw (from head vs capacity curve for water) = 34.62 m
The efficiency
(from efficiency vs capacity curve for water) = 0.76
Viscosity of oil, µ = 220 cSt
The corresponding capacity, head and efficiency are:
Qoil = CQ x QW = 0.95 x 102 = 96.9 m3/h
Hoil = CH x HW = 0.96 x 34.62 = 33.235 m
Figure 16-59c. Performance Correction Chart (Source: The Hydraulic Institute, USA)
= 0.645 x 0.76 = 0.4902
The power required by the pump when it handles the oil is:
QNW, m3/h | 170
Density of oil, kg/m3 | 900
Using Figures 16 - 59c and 16-62, the Revised Performance of Centrifugal Pump for Handling Oil
| 0.6 x QNW | 0.8 x QNW | 1.0 x QNW | 1.2 x QNW
Q, m3/h | 102 | 136 | 170 | 204
H, m | 34.62 | 33.21 | 31 | 27.3
ηW | 0.76 | 0.84 | 0.86 | 0.85
CQ | 0.95 | 0.95 | 0.95 | 0.95
CH | 0.96 | 0.94 | 0.92 | 0.895
CE | 0.645 | 0.645 | 0.645 | 0.645 | Figure 16-62. Sample performance curve
Qoil, m3/h | 96.9 | 129.2 | 161.5 | 193.8
Hoil, m | 33.2352 | 31.2174 | 28.52 | 24.4335
ηoil | 0.4902 | 0.5418 | 0.5547 | 0.54825
P, kW | 16.11 | 18.26 | 20.36 | 21.18